## Description
Cerberus FIT
Field Bus Devices & Fire Panels
Lists of Compatibility | Special Test effort Prio 1 / 2 / 3;
Reference: 704-006-004 - Rev. 193
Siemens Switzerland Ltd. Building Technologies Division International Headquarters Gubelstrasse 22 CH-6300 Zug Tel. +41 41 724-2424
www.siemens.com/buildingtechnologies
© Siemens Switzerland Ltd 2016

## C-NET
|  |  |  | Cerberus FIT |  | Additional Tools | [7 empty] | Dev. Funct.
| C-NET Devices & Fire Panels List of Compatibility |  |  | FC360 | MP1 | Line Tester | FDUL221, FW status 2.5.6 | FDUL221, FW status 3.1.9 | FDUL221, FW status 3.3.2 | FDUL221, FW status 3.4.0 | FDUL221, FW status 3.4.5 | FDUL221, FW status 3.6.2 / 3.6.3 | FDUL221, FW status 4.1.1 / 4.1.2 | Turbo isolator for fast short circuit recovery | Steady-on AI feature | Extended Status indication feature | Extended Status indication feature supported by panel SW
| Special Detectors |  | Customer Text |  |  | CustomerText
| (all) | Special detector, ES ≥ 40 | - |  | - | - | - | - | - | - | - | - | - | x | x | 0 | 0
| FDF221-9 | Infrared flame detector (1 sensor), DualProtocol Collective | FDF221 |  | 0 | FDF221 | x | x | x | x | x | x | x | 0 | 0 | ↑ | ↑
| FDF241-9 | Infrared flame detector (2 sensors / 1 photo diode), DualProtocol Collective | FDF241 |  | x | FDF241 | x | x | x | x | x | x | x | 0 | 0 | ↑ | ↑
| FDL241-9 | Linear smoke detector, DualProtocol Collective | FDL241 |  | x | FDL241 | x | x | x | x | x | x | x | 0 | ↑ | ↑ | ↑
| Manual Call Points |  | Customer Text |  |  | CustomerText
| (all) | Manual call point, ES ≥ 40 | - |  | - | - | - | - | - | - | - | - | - | x | x | 0 | 0
| FDM221 | Manual call point, direct action | FDM221 |  | x | FDM221 | x | x | x | x | x | x | x | 0 | 0 | ↑ | ↑
| FDM225 | Manual call point, direct action | FDM225/6 |  | x | FDM225/6 | (x)/R69 | x | x | x | x | x | x | 0 | 0 | ↑ | ↑
| FDM226 | Manual call point, direct action | FDM225/6 |  | x | FDM225/6 | (x)/R69 | x | x | x | x | x | x | 0 | 0 | ↑ | ↑
| FDM231 | Manual call point, direct action | FDM231 |  | x | FDM231 | (x)/R69 | (x)/R69 | (x)/R69 | (x)/R69 | (x)/R69 | (x)/R69 | x | 0 | x | x | ↑
| FDM223 | Manual call point, indirect action | FDM223 |  | x | FDM223 | x | x | x | x | x | x | x | ↑ | ↑ | ↑ | ↑
| FDM233 | Manual call point (migration), indirect action | FDM233 |  | (0) | FDM233 | R64 | R64 | R64 | R64 | R64 | R64 | x | x | ↑ | ↑ | ↑
| FDM243H | Manual call point (Vershoven), indirect action | FDM243H |  | (0) | FDM243H | R64 | R64 | R64 | R64 | R64 | R64 | x | x | ↑ | ↑ | ↑
| FDM223-Ex | Manual call point, indirect action (intrinsically safe) | FDM223-Ex |  | (0) | FDM223Ex | R64 | R64 | R64 | R64 | R64 | R64 | x | x | x | ↑ | ↑
| FDM224 | Manual call point, direct action | FDM224 |  | x | FDM224 | x | x | x | x | x | x | x | ↑ | ↑ | ↑ | ↑
| FDM234 | Manual call point (migration), direct action | FDM234 |  | (0) | FDM234 | R68 | R68 | R68 | R68 | R68 | R68 | x | x | ↑ | ↑ | ↑
| Radio Devices (Wireless Telerex/SIGMASPACE) |  | Customer Text |  |  | CustomerText
| DOW1171 | Radio smoke detector, ES < 8 | DOW1171 |  | 0 | DOW1171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | n | 0 | 0 | 0
| DOW1171 | Radio smoke detector, ES ≥ 8 | DOW1171 |  | 0 | DOW1171 | 0 | x | x | x | x | x | x | n | 0 | 0 | 0
| SMF6120 | Radio manual call point | SMF6120 |  | 0 | SMF6120 | 0 | x | x | x | x | x | x | n | 0 | 0 | 0
| FDCW221 | Radio gateway, ES < 40 | FDCW221 |  | 0 | FDCW221 | 0 | x | x | x | x | x | x | 0 | 0 | 0 | 0
| FDCW221 | Radio gateway, VdS EN54-25 full compatible, ES ≥ 40 | ↑ |  | 0 | FDCW221 | 0 | x | x | x | x | x | x | ↑ | ↑ | ↑ | ↑
| FDCW221 | Line separator inside 'radio gateway' | FDCL221v |  | 0 | FDCL221v | 0 | R66 | x | x | x | x | x | 0 | 0 | 0 | 0
| Radio Devices (SWING) |  | Customer Text |  |  | CustomerText
| FDOOT271 | Radio neural fire detector | FDOOT271 |  | 0 | FDOOT271 | 0 | 0 | 0 | 0 | x | x | x | n | 0 | 0 | 0
| FDM273 | Radio manual call point, indirect action | FDM273 |  | 0 | FDM273 | 0 | 0 | 0 | 0 | 0 | x | x | n | 0 | x | 0
| FDM275 | Radio manual call point, direct action | FDM275 |  | 0 | FDM275 | 0 | 0 | 0 | 0 | 0 | 0 | x | n | 0 | x | 0
| FDCW241 | Radio gateway | FDCW241 |  | 0 | FDCW241 | 0 | 0 | 0 | 0 | x | x | x | x | 0 | x | 0
| FDCW241 | Line separator inside 'radio gateway' | FDCL221v |  | 0 | FDCL221v | 0 | 0 | 0 | 0 | x | x | x | x | 0 | n | n
| Line Modules |  | Customer Text |  |  | CustomerText
| (all) | Line module, ES < 30 | - |  | R2 | - | - | - | - | - | - | - | - | 0 | n | 0 | 0
| (all) | Line module, ES ≥ 40 | - |  | - | - | - | - | - | - | - | - | - | x | n | 0 | 0
| FDCI221 | Input module (1 input) | FDCI221 |  | x | FDCI221 | 0 | 0 | 0 | x | x | x | x | x | n | ↑ | ↑
| FDCI222 | Input module (4 inputs) | FDCI222 |  | x | FDCI222 | x | x | x | x | x | x | x | ↑ | n | ↑ | ↑
| FDCIO221 | In/Output module (1 input & 1 output) | FDCIO221 |  | x | FDCIO221 | 0 | 0 | 0 | x | x | x | x | x | n | ↑ | ↑
| FDCIO222 | In/Output module (4 inputs & 4 outputs), ES < 8 | FDCIO222 |  | x/R1 | FDCIO222 | x | x | x | x | x | x | x | ↑ | n | ↑ | ↑
| FDCIO222 | In/Output module (4 inputs & 4 outputs), ES ≥ 8 | ↑ |  | x/R2 | ↑ | x | x | x | x | x | x | x | ↑ | n | ↑ | ↑
| FDCIO223 | In/Output module (2 inputs or outputs) (Transponder), ES < 41 | FDCIO223 |  | 0 | FDCIO223 | 0 | x | x | x | x | x | x | ↑ | n | ↑ | ↑
| FDCIO223 | In/Output module (2 inputs or outputs) (Transponder), ES ≥ 41, ≤ 45 | ↑ |  | 0 | ↑ | 0 | x | x | x | x | x | x | x | n | ↑ | ↑
| FDCIO223 | In/Output module (2 inputs or outputs) (Transponder), ES ≥ 50 | ↑ |  | 0 | ↑ | 0 | x | x | x | x | x | x | x | n | ↑ | ↑
| FDCIO224 | In/Output module (4 inputs & 4 outputs) | FDCIO224 |  | x/R2 | FDCIO224 | 0 | x | x | x | x | x | x | ↑ | n | ↑ | ↑
| FDCL221 | Line separator | FDCL221 |  | x | FDCL221 | x | x | x | x | x | x | x | ↑ | n | ↑ | ↑
| FDCL221-M | Multi line separator module (8 - 9 isolators) | FDCL221M |  | x | FDCL221-M | R66 | R66 | R66 | x | x | x | x | x | n | ↑ | ↑
| FDCL221-Ex | Line adapter (intrinsically safe) | FDCL221-Ex |  | (0) | FDCL221-Ex | x | x | x | x | x | x | x | x | n | ↑ | ↑
| Integrated Modules |  | Customer Text |  |  | CustomerText
| VLF-250 / VLF-500 | Vesda LaserFOCUS (ASD) | FDCIO222 ASD |  | (0) | VLF250/500 | R30 | x | x | x | x | x | x | 0 | n | 0 | 0
| FDA221 | Siemens aspiration smoke detector (ASD) C-Line | FDA221 |  | 0 | FDA221 | 0 | 0 | 0 | 0 | x | x | x | 0 | x | 0 | 0
| FDA241 | Siemens aspiration smoke detector (ASD) S-Line | FDA241 |  | 0 | FDA241 | 0 | 0 | 0 | 0 | x | x | x | 0 | x | 0 | 0
| Alarm Devices |  | Customer Text |  |  | CustomerText
| (all) | Sounder, ES < 30 | - |  | - | - | - | - | - | - | - | - | - | 0 | 0 | 0 | -
| (all) | Sounder, ES ≥ 30, < 40 | - |  | - | - | - | - | - | - | - | - | - | 0 | 0 | 0 | -
| (all) | Sounder, ES ≥ 40 | - |  | - | - | - | - | - | - | - | - | - | x | 0 | 0 | -
| FDS221-R | Alarm sounder red, ES ≤ 31 | FDS221 |  | x/R9-R12 | FDS221 | x | x | x | x | x | x | x | ↑ | 0 | 0 | 0
| FDS221-R | Alarm sounder red, ES > 31 | ↑ |  | x | ↑ | x | x | x | x | x | x | x | ↑ | ↑ | ↑ | ↑
| FDS221-W | Alarm sounder white, ES ≤ 31 | FDS221 |  | x/R9-R12 | FDS221 | x | x | x | x | x | x | x | ↑ | 0 | 0 | 0
| FDS221-W | Alarm sounder white, ES > 31 | ↑ |  | x | ↑ | x | x | x | x | x | x | x | ↑ | ↑ | ↑ | ↑
| FDS229-A | Sounder beacon amber | FDS229 |  | x | FDS229-A | 0 | R60 | x | x | x | x | x | x | 0 | x | 0
| FDS229-R | Alarm sounder beacon red | FDS229 |  | x | FDS229-R | 0 | R60 | x | x | x | x | x | x | 0 | x | 0
| Operation and Indication Devices |  | Customer Text |  |  | CustomerText
| FT2001 | Mimic display driver | FT2001 |  | 0 | FT2001 | 0 | x | x | x | x | x | x | x | n | 0 | 0
| FT2010 | Floor repeater terminal (FRT), ES < 8 | FT2010 |  | 0 | FT2010 | 0 | x | x | x | x | x | x | 0 | n | 0 | 0
| FT2010 | Floor repeater terminal (FRT), ES ≥ 8 | ↑ |  | x/R22 | ↑ | 0 | x | x | x | x | x | x | x | ↑ | ↑ | ↑
| FT2011 | Floor repeater display (FRD), ES < 8 | FT2011 |  | 0 | FT2011 | 0 | x | x | x | x | x | x | 0 | n | 0 | 0
| FT2011 | Floor repeater display (FRD), ES ≥ 8 | ↑ |  | x/R22 | ↑ | 0 | x | x | x | x | x | x | x | ↑ | ↑ | ↑
| FDCAI221 | Addressable alarm indicator | FDCAI221 |  | x | FDCAI221 | 0 | 0 | 0 | 0 | x | x | x | x | n | 0 | 0
| Point Detectors |  | Customer Text |  |  | CustomerText
| HI722 | Heat detector (static) | HI722 |  | x | HI722 | 0 | 0 | 0 | x | x | x | x | x | x | 0 | 0
| HI720 | Heat detector (static+ROR) | HI720 |  | x | HI720 | 0 | 0 | 0 | x | x | x | x | x | x | 0 | 0
| OH720 | Multi-sensor smoke detector, ES < 10 | OH720 |  | x | OH720 | 0 | 0 | 0 | x | x | x | x | x | x | 0 | 0
| OH720 | Multi-sensor smoke detector with soiling report support, ES ≥ 10 | ↑ |  | x/R43 | ↑ | 0 | 0 | 0 | x | x | x | x | ↑ | ↑ | x | x
| OOH740 | Multi-sensor smoke detector; DualProtocol Collective, ES < 20 | OOH740 |  | x | OOH740 | 0 | 0 | 0 | 0 | x | x | x | x | 0 | 0 | 0
| OOH740 | Multi-sensor smoke detector with ambient supervision, additional parameter sets and soiling report suppot, DualProtocol Collective, ES ≥ 20 | ↑ |  | x/R43/ R44/ R45 | ↑ | 0 | 0 | 0 | 0 | x | x | x | ↑ | x | x | x
| OOH740-A9-Ex | Multi-sensor detector with ambient supervision and soiling (intrinsically safe), DualProtocol Collective | OOH740-Ex |  | (0) | OOH740Ex | 0 | 0 | 0 | 0 | x | x | x | x | 0 | 0 | 0
| OP720 | Smoke detector, ES < 10 | OP720 |  | x | OP720 | 0 | 0 | 0 | x | x | x | x | x | x | 0 | 0
| OP720 | Smoke detector with soiling report support, ES ≥ 10 | ↑ |  | x/R43 | ↑ | 0 | 0 | 0 | x | x | x | x | ↑ | ↑ | x | x
| Special Detectors |  | Customer Text |  |  | CustomerText
| OOHC740 | Neural fire and CO detector with ambient supervision, ES < 20 | OOHC740 |  | x/R44 | OOHC740 | 0 | 0 | 0 | 0 | x | x | x | x | 0 | 0 | 0
| OOHC740 | Neural fire and CO detector with ambient supervision and soiling report support, ES ≥ 20 | ↑ |  | x/R43/ R44 | ↑ | 0 | 0 | 0 | 0 | x | x | x | ↑ | x | x | x
| Alarm Devices |  | Customer Text |  |  | CustomerText
| DBS721 | Sounder interbase | DBS721 |  | x | DBS721 | R59 | R59 | R59 | R59 | R59 | x | x | x | n | n | n
| DBS728 | Sounder beacon interbase (supports EN54-23) | DBS728 |  | x | DBS728 | R60 | R60 | R60 | R60 | R60 | R60 | R60 | x | n | n | n
| DBS729 | Sounder beacon interbase | DBS729 |  | x | DBS729 | R60 | R60 | R60 | R60 | R60 | x | x | x | n | n | n
| Line Modules |  | Customer Text |  |  | CustomerText
| FDCI723 | Zone module, ext. powered (1 collective line) | FDCI723 |  | x | FDCI723 | 0 | 0 | 0 | 0 | 0 | 0 | x | x | n | 0 | 0
| Base Accessories |  | Customer Text |  |  | CustomerText
| DB721D | Detector base collective with remove diode unit | - |  | (0) | - | - | - | - | - | - | - | - | n | n | n | n
| Alarm Devices |  | Customer Text |  |  | CustomerText
| DBS720 | Sounder base | Sounder Base |  | x | [note symbol on the device] | 0 | 0 | 0 | x | x | x | x | n | n | n | n
| Base Accessories |  | Customer Text |  |  | CustomerText
| DB721 | Detector base with loop contact | - |  | x | - | - | - | - | - | - | - | - | n | n | n | n
| DB722 | Detector base | - |  | x/R23 | - | - | - | - | - | - | - | - | n | n | n | n
Panel System Functions
| Turbo isolator for fast short circuit recovery |  |  |  | x |  | n | n | n | n | n | n | n
| Device firmware update in field possible |  |  |  | 0 |  | 0 | N31 | N31 | N31 | N31 | N31 | N31
| Fast read-in of base sounders during commissioning (if device AND base sounder ES ≥ 30) |  |  |  | x |  | 0 | x | x | x | x | x | x
| Strobe configurable (e.g. 'strobe only' or 'sound only') |  |  |  | x |  | n | n | n | n | n | n | n
| Brandfallsteuerung gemäss VdS (Feststellanlagen) |  |  |  | 0 |  | n | n | n | n | n | n | n
| Use to connect collective/conventional devices over field device |  |  |  | x |  | n | n | n | n | n | n | n
| Configurable parameter set |  |  |  | x |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Support soiling report |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Status indication with internal AI for Russia / India (steady-on for alarm/active) |  |  |  | x |  | - | - | - | - | - | - | -
| Enhanced status indication with internal & external AI for Russia / India via device configuration |  |  |  | 0 |  | - | - | - | - | - | - | -
| CO part usable with full functionality |  |  |  | x/R79 |  | n | n | n | n | n | n | n
| Support of ambient supervision channel |  |  |  | 0 |  | n | n | n | n | n | n | x
x | compatible
(x) | compatible with some restrictions/limitations
t | tested (commissioned, silenceness, alarm/activation)
R | Restrictions apply, see comment or restriction sheet
0 | not compatible
no data available
n | not applicable
↑ | see in the 1 -3 entries in bold font further above.
Notes:
| ES | Product version (Erzeugnisstand).
| FW | Firmware version aka 'SW version' aka 'FW revision'.
| Customer Text | Representation on the panel display and in the tools; Bold frame = compatible devices with maybe limited functionality.
| (all) | Bold font entries are valid for all devices in the same block, that means the entry is device type independent.
| N31 | Update of FDUL itself possible. Not of devices like e.g. FRT or Mimic.

## C-NET restrictions
C-NET Devices List of Restrictions |  |  |  | Special Test effort Prio 1 / 2 / 3;
Some restrictions concerning C-NET devices only apply with specific product versions and some functions are only available with specific product versions (also known as “ES” or “device version”) and higher.
R3
Refe-rence | Device Type | Product Version | Restriction
R1 | FDCIOxxx except FDCIO223 | < 8 | The ‘Fail safe mode’ of outputs does not work correctly. It is strongly recommended to set all outputs to mode ‘Freeze (no change)’.
R2 | FDCIOxxx except FDCIO223 | < 30 | The ‘Fail safe mode’ ‘Activated by sounder cmd. upon degraded alarm’ is not supported. If this mode is configured the device reports a fault.
R9 | FDS221-R, FDS221-W | < 30 | The sounder commands on the line upon a degraded alarm are not supported → the sounder will not be activated upon a degraded alarm.
R10 | FDS221-R, FDS221-W | ≥ 30 | Some of the tones have been changed in the “2nd device generation”. The selection list in the Engineering tool describes the 1st generation tones. Please see documentation (007025) for information about the current tones.
R11 | FDS221-R, FDS221-W | 30 | Tone 4 ‘Sweep-up, linear, 540 -> 1200Hz [NEN2575]’ is not to be used. If this tone is configured the loop sounder might not be activated in case of an event.
R12 | FDS221-R, FDS221-W | 31 | Tone 4 ‘Sweep-up, linear, 540 -> 1200Hz [NEN2575]’ cannot be used → if tone 4 is configured it is automatically replaced with tone 10 ‘Sweep-up, linear, 540 -> 1200Hz [AS2220]’
which is very similar to tone 4. This is a temporary solution in this product version only.
R22 | FT2010 (FRT), FT2011 (FRD) | all | see panel release notes for further details according to compatibility FW version to ES
R23 | DB722 | all | When the detector is removed from the line, the communication between the control panel and the next detector is interrupted. In this case, alarming by the subsequent detectors is no longer guaranteed and replacement could fail.
R30 | VLF-250 / VLF-500, FDV241 | all | Customer Text = FDCIO222. Device is visible as normal IO module and so no speciality device functionality is available
R43 | various | all | no soiling report support
R44 | various | all | no support of ambient supervision channel
R45 | various | all | no support of new parameter sets
R59 | FDSB221 | all | Customer Text = FDS221
R60 | FDS229-A, FDS229-R, etc. | all | Customer Text = FDS229
R64 | FDM233, FDM243H, FDM223-Ex | all | Customer Text = FDM223
R66 | FDCL221-M, FDCL221-Ex | all | Customer Text = FDCL221
R68 | FDM234 | all | Customer Text = FDM224
R69 | FDM225, FDM226, FDM231 | all | Customer Text = FDM221
R79 | Device with CO part as e.g. OOHC740 | all | only limited support, see corresponding panel manual for more details

## Collective
|  |  |  | Line Devices |  |  |  | Collective Functions
| Collective / Conventional Devices & Fire Panels List of Compatibility |  |  | With secondary field bus | FDCI723 - collective | FDCI723 - conventional | FDCI723 - collective Ex | Allowed system functions | Config: Short circuit = ALARM allowed | Config: Pulse Memory (Alarm Verification) allowed | Config: "Nordic" option (not implemented) allowed | Config: 'British standard' allowed | Device functions | Connection factor KMK (see remark R4) | Alarm load (S: short circuit; Z: Zener; R: Resistor)
MS7
Bases
| Z74 | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z74A | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| B721 | base |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
Detectors
| D702 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D712 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D715 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D716 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D726 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| F712 / BR712 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| F712V | Ioni smoke verifying |  |  | 0 | 0 | 0 |  |  | 0 | 0 | n |  | 0 | Z
| F715 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.5, R4 | Z
| F716 / BR716 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F716I | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F716V | Ioni smoke |  |  | 0 | 0 | 0 |  | x | R5 | x | n |  | 1, R4 | Z
| F716VI | Ioni smoke |  |  | 0 | 0 | 0 |  | x | R5 | x | n |  | 1, R4 | Z
| F721 | Ioni smoke |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 0 | n
| F725 (~F715) | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| F726 / BR20 (~F716) | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| F732 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F736 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| R700 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.5 | Z
| R716 / BR17 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| R716H | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| RT716H | Smoke detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 0 | Z
| R716I | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | R5 | x | n |  | 1 | Z
| R716VI | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | R5 | x | n |  | 1 | Z
MS9
Bases
| Z90 | Detector base w. internal AI |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z90D | Detector base w. int. and ext. AI |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z90B | Detector base w. EMC/surge prot. |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z91C | Det. base Ex w. int. & ext. AI |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z94 | Detector base w. internal AI |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z94B | Detector base w. EMC/surge prot. |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z94C | Det. base Ex w. int. & ext. AI |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z94D | Detector base w. int. and ext. AI |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| Z96 | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
Detectors
| BM957 | Heat max |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 1 | Z
| BM980 | Heat max |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 1 | Z
| BD957 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D900 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D901 EX | Heat rate of rise, Ex device |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| D915 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D920 | Heat rate of rise |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D921 EX | Heat rate of rise, Ex device |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| BR10 | Optical smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| BR12 | Optical smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| BR12 Ex | Optical smoke, Ex device |  |  | 0 | 0 | 0 |  |  | n | 0 | n |  | n | R
| F905 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F906 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F910 / BR910 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F911 EX | Ioni smoke, Ex device |  |  | 0 | 0 | 0 |  |  | n | 0 | n |  |  | R
| F915 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F922 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| F930 | Ioni smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R4 | Z
| R902 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| R906 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| R910 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R922 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
| R925 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R930 | Scattered light smoke (R13) |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R930H | Scattered light smoke (R13) |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R936 | Scattered light smoke (R13) |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R936H | Scattered light smoke (R13) |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R937 | Scattered light smoke (R13) |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1.25 | Z
| R970 | Scattered light smoke |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1 | Z
Manual Call Points
| AT40 | Manual call point |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
| AT41 | Manual call point |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
| AT50 | Manual call point |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
| AT51 | Manual call point |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
| ATAN50 | Manual call point |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
Special Detectors MS24
Detectors
| A2400 | Linear smoke detector |  |  | 0 | 0 | 0 |  | x | R5 | x | n |  | 15, R6 | Z
| D2401 | Rate of rise detector (heat max) |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| D2401 EX | Heat max, Ex device |  |  | 0 | 0 | 0 |  |  | n | 0 | n |  | n | R
| D2409 | Maximum heat detector |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 0.01 | Z
| D2410 | Maximum heat detector |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 0.01 | Z
| D2417 | Max. temperature detector |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
| S2406 | Flame detector |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 5 | Z
| S2406 EX | Flame detector, Ex device |  |  | 0 | 0 | 0 |  |  | n | 0 | n |  | n | R
| T2416 | Maximum heat detector |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 1 | Z
| T2418 | Maximum heat detector |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 3.5, R3 | Z
Various Devices
| SE20 | latching circuit (old version) |  |  | v | 0 | 0 |  | x | n | x | n |  | 0.01 | Z
| SE22 | latching circuit (new version) |  |  | nv | 0 | 0 |  | x | n | x | n |  | 0.01 | Z
| SPB3 | sprinkler test-box |  |  | nv | 0 | 0 |  | x | n | ? | n |  | 1 | Z
Multiprotocol Devices
Bases
| FDB201 / FDB202 | Detector base Sinteso |  |  | x | x | x |  | n | n | n | 0 |  | 0 | n
| DB721 / DB721D | Detector base Cerberus |  |  | x | x | 0 |  | n | n | n | 0 |  | 0 | n
| FDB299 | Base adapter MPD to AlgoRex/ SigmaCon (DB1101A or SPF600 |  |  | 0 | 0 | 0 |  | n | n | n | 0 |  | 0 | n
Detectors
| FDOOT241-9M | Neural fire detector, A5Q00015955, ES ≥ 13 |  |  | x | x | 0 |  | R14 | R5 | x | n |  | 2, R8 | ZR
| FDOOT241-9 | Neural fire detector, A5Q00004813, ES < 30 |  |  | x | x | 0 |  | R14 | R5 | x | n |  | 2 | ZR
| FDOOT241-9 | Neural fire detector, A5Q00004813, ES ≥ 30 |  |  | x | x | 0 |  | R14 | R5 | x | n |  | 1.5, R8 | ZR
| FDOOT241-A9 | Neural fire detector |  |  | x | x | 0 |  | R14 | R5 | x | n |  | 1.25, R20 | ZR
| FDOOT241-A9-Ex | Neural fire detector (intrinsically safe) |  |  | 0 | 0 | x |  | R14 | n | n | n |  | 1.25, R20 | Z
| OOH740 | Multi sensor detector |  |  | x | x | 0 |  | R14 | R5 | x | n |  | 1.25, R20 | ZR
| OOH740-A9-Ex | Neural fire detector (intrinsically safe) |  |  | 0 | 0 | x |  | R14 | n | n | n |  | 1.25, R20 | Z
| FDF221-9 | Flame detector, ES < 30 |  |  | x/R16 | x/R16 | 0 |  | R14 | R5 | x | n |  | 5 | ZR
| FDF221-9 | Flame detector, ES ≥ 30 |  |  | x/R16 | x/R16 | 0 |  | R14 | R5 | x | n |  | 5 | ZR
| FDF241-9 | Flame detector, ES < 30 |  |  | x/R16 | x/R16 | 0 |  | R14 | R5 | x | n |  | 5 | ZR
| FDF241-9 | Flame detector, ES ≥ 30 |  |  | x/R16 | x/R16 | 0 |  | R14 | R5 | x | n |  | 5 | ZR
| FDL241-9 | Linear smoke detector, ES < 30 |  |  | x/R16 | x/R16 | 0 |  | R14 | R5 | x | n |  | 10 | ZR
| FDL241-9 | Linear smoke detector, ES ≥ 30 |  |  | x/R16 | x/R16 | 0 |  | R14 | R5 | x | n |  | 10 | ZR
Alarm Devices
| FDSB292 | Sounder base collective |  |  | 0 | 0 | 0 |  | 0 | R5 | n | 0 |  | 1.5 | n
DS11 / SynoLINE600 / SigmaCon (Collective)
Bases
| DB1101A / DB1102A | Detector base for DS11 |  |  | x | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| SO620C | Detector base for SynoLINE600 |  |  | x | 0 | 0 |  | n | n | n | 0 |  | 0 | n
| SPF600 | Detector base for SigmaCon |  |  | (0) | 0 | 0 |  | n | n | n | 0 |  | 0 | n
Detectors
| DF1101-EX | Flame detector, Ex device |  |  | 0 | 0 | x |  |  | n | n | n |  |  | R
| DO1101A / OP620C / SDF200 | Smoke detector |  |  | x/ R37 | 0 | 0 |  | x | x | x | n |  | 1, R9 | Z
| DO1101A-Ex | Smoke, Ex device |  |  | 0 | 0 | x |  |  | n | n | n |  |  | R
| DO1102A | Smoke detector |  |  | x | 0 | 0 |  | x | x | x | n |  | 1, R9 | Z
| DO1103A | Smoke detector |  |  | x | 0 | 0 |  | x | x | x | n |  | 1, R9 | Z
| DO1104A / OP624C | Smoke detector |  |  | x | 0 | 0 |  | x | x | x | n |  | 1, R9 | Z
| DT1101A / HI620C / SDT210 | Heat detector |  |  | x/ R37 | 0 | 0 |  | x | x/0/N2 | x | n |  | 1 | Z
| DT1101/02A -Ex | Heat detector, Ex device |  |  | 0 | 0 | x |  |  | n | 0 | n |  |  | R
| DT1102A / HI622C | Heat detector |  |  | x | 0 | 0 |  | x | x/0/N2 | x | n |  | 1 | Z
| HI364C | Rate of rise heat detector |  |  | 0 | 0 | 0 |  | x | x/0/N2 | x | n |  | 1 | Z
| OP364C | Smoke detector |  |  | 0 | 0 | 0 |  | x | x | x | n |  | 1, R9 | Z
Manual Call Points
| DM1101 / MT620C | Manual call point |  |  | x | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
| DM1103 / DM1104 / MT622C / MT624C | Manual call point |  |  | x | 0 | 0 |  | x | n | 0 | n |  | 0.01 | Z
| FDM1101 / FDM1101-RG / -RP | Manual call point |  |  | x | 0 | x |  | x | n | 0 | n |  | 0.01 | Z
| SIGMACON RT-FW (V24217-Ax2xx+C156) | Manual call point ("Springknopf") |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | R
| SIGMACON RT-FW (V24217-Bx2xx) | Manual call point ("Druckknopf") |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | R
| SIGMACON RT-FW (V24217-Cx2xx) | Manual call point ("Designer Druckknopf") |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 0.01 | R
Alarm Devices
| DBZ1195A | Acoustic base |  |  | x | 0 | 0 |  | n | n | n | n |  | 0 | n
Operation and Indication Devices
| DC1192 | Interface to Ex barrier |  |  | 0 | 0 | 0 |  | x | n | 0 | n |  | 1 | Z
| CB319A | Input device |  |  | 0 | 0 | 0 |  | x | n | x | n |  | 1 | Z
| CB320A | Input device |  |  | 0 | 0 | 0 |  | x | n | x | n |  | 1 | Z
Special Detectors DS11 / SynoLINE600
Detectors
| DLO1191A | Linear smoke detector |  |  | 0 | 0 | 0 |  | x | x | x | x |  | 25, R11 | ZR
| DF1191 | Flame detector (1 sensor) |  |  | x | 0 | 0 |  | x | x | x | x |  | 6 | Z
| DF1192 | Flame detector (3 sensors) |  |  | x | 0 | 0 |  | x | x | x | x |  | 6 | Z
Short-Circuit Devices
Detectors
| KEA2002 | Heat detector |  |  | 0 | 0 | 0 |  | x | 0 | 0 | 0 |  |  | S
| KEA2003 | Heat detector |  |  | 0 | 0 | 0 |  | x | 0 | 0 | 0 |  |  | S
| KEA2013 | Heat detector |  |  | 0 | 0 | 0 |  | x | 0 | 0 | 0 |  |  | S
| SWM1KL/150 | Heat detector |  |  | 0 | 0 | 0 |  | x | 0 | 0 | 0 |  |  | S
Manual Call Points
| KEB12201 | Manual call point |  |  | 0 | 0 | 0 |  | x | 0 | x | x |  | 0.01 | S
| MCP3A | Manual call point |  |  | 0 | 0 | 0 |  | x | 0 | x | x |  | 0.01 | S
SynoLINE300 (Conventional)
Bases
| SO320 | Detector base for SynoLINE300 |  |  | 0 | x | 0 |  | n | n | n | n |  | 0 | n
Detectors
| HI320C | Heat detector |  |  | 0 | x | 0 |  | x | x/0/N2 | 0 | 0 |  | 1 | R
| HI322C | Heat detector |  |  | 0 | x | 0 |  | x | x/0/N2 | 0 | 0 |  | 1 | R
| OP320C | Smoke detector |  |  | 0 | x | 0 |  | x | x | 0 | 0 |  | 1 | R
| OH320C | Smoke detector multi sensor |  |  | 0 | x | 0 |  | x | x | 0 | 0 |  | 1 | R
Manual Call Points
| MT320C | Manual call point Synova 300 |  |  | 0 | x | 0 |  | x |  | 0 | 0 |  | 0.01 | R
| FDM1101A-RG / -RP | Manual call point glass / plastic |  |  | 0 | x | 0 |  | x |  | R36 | R36 |  | 0.01 | SR
Apollo (Conventional)
Bases
| TimeSaver Base | Order# ORB-MB-00001-APO |  |  | 0 | x | 0 |  | n | n | n | n |  | 0 | n
| TimeSaver Deep Base | Order# ORB-MB-00019-APO |  |  | 0 | x | 0 |  | n | n | n | n |  | 0 | n
| TimeSaver Diode Base | Order# ORB-DB-00003-APO |  |  | 0 | x/ R38 | 0 |  | n | n | n | n |  | 0 | n
Detectors
| Orbis Optical | Order# ORB-OP-1200x-APO |  |  | 0 | x | 0 |  | x | x | 0 | 0 |  | 1 | R
| Orbis Multisensor | Order# ORB-OH-1300x-APO |  |  | 0 | x | 0 |  | x | x | 0 | 0 |  | 1 | R
| Orbis A1R or A2S | Order# ORB-HT-11xxx-APO |  |  | 0 | x | 0 |  | x | x | 0 | 0 |  | 1 | R
Detector Series
| Series 60 detectors | Base |  |  | 0 | x | 0 |  | n | n | n | n |  | 0 | n
| Series 60 detectors | Series of detectors |  |  | 0 | x | 0 |  |  |  | 0 | 0 |  |  | R
| Series 65 detectors | Standard Base |  |  | 0 | x | 0 |  | n | n | n | n |  | 0 | n
| Series 65 detectors | Diode Base |  |  | 0 | x | 0 |  | n | n | n | n |  | 0 | n
| Series 65 detectors | Series of detectors |  |  | 0 | x | 0 |  | x | x | 0 | 0 |  | 1 | R
MS6
Detectors
| D600 / D610 | Heat detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| D6A | Heat detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| D6A Ex | Heat detector, Ex device |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| F600 / F605 | Ionisation smoke detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 0.8 | R
| F6A | Ionisation smoke detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| F6A Ex | Ionisation smoke detector, Ex |  |  | 0 | 0 | 0 |  |  | n | n | n |  |  | R
| R610 | Smoke detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 1.5 | R
| S600 | Flame detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 2.5 | R
| S601 | Spark detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 2.5 | R
| S610 | Flame detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 2.5 | R
| S620 | Flame detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 5 | R
| S6A | Flame detector |  |  | 0 | 0 | 0 |  |  | n | n | n |  | 2.5 | R
FD18C (EN)
Bases
| DB110 | Detector base |  |  | x | x | 0 |  | n | n | n | 0 |  | 0 | n
| DB110D | Detector base with continuity diode |  |  | x | x | 0 |  | n | n | n | x |  | 0 | n
| DB110R | Detector base with parameter set resistor |  |  | x | x | 0 |  | n | n | n | 0 |  | 0 | n
| DB110RD | Detector base with continuity diode and parameter set resistor |  |  | x | x | 0 |  | n | n | n | x |  | 0 | n
Detectors
| OH110 | Multi sensor detector |  |  | x | x | 0 |  | x | x | n | n |  | 1 | ZR
| OP110 | Smoke detector |  |  | x | x | 0 |  | x | x | n | n |  | 1 | ZR
| HI110 | Heat detector |  |  | x | x | 0 |  | x | x/0/N2 | n | n |  | 1 | ZR
| HI112 | Heat detector |  |  | x | x | 0 |  | x | x/0/N2 | n | n |  | 1 | ZR
Miscellaneous
Bases
| FDB221 | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | n
| FDB221-AA | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | n
| FPE90D | FPK9 base electronics |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | n
| Z70xx | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | n
| Z72xx | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | n
| ZAJ.. | Detector base |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | n
Detectors
| HI520/OP520 | Collective heat / smoke detector |  |  | 0 | 0 | 0 |  |  |  |  | n |  |  | R
| FDO181C/FDT181C | Collective smoke / heat detector |  |  | 0 | 0 | 0 |  |  |  |  | n |  |  | R
Various Devices
| K5M020 | MS5 adapter |  |  | 0 | 0 | 0 |  | n | n | n | n |  |  | Z
| MLK20 | Meldelinienkoppler |  |  | 0 | 0 | 0 |  | n | n | n | n |  |  | Z
| SE2 | EMC protection for AT4x/5x |  |  | 0 | 0 | 0 |  | n | n | n | n |  | 0 | Z
| SB3 | Safety barrier (Ex-barrier) |  |  | 0 | 0 | x |  | n | n | n | n |  | 0 | Z
Panel System Functions
| Config: Short circuit = ALARM |  |  |  | 0 | 0 | 0
| Config: Pulse memory |  |  |  | x | x | x
| Config: "Nordic" option |  |  |  | 0 | 0 | 0
| Config: "Automatic / manual discrimination" option |  |  |  | 0 | 0 | 0
| Config: British standard |  |  |  | x | x | x
| Line shortcut detection |  |  |  | x | x | x
| Line break detection |  |  |  | x | x | x
| Earth fault detection, handling |  |  |  | x | x | x
| High leak current detection |  |  |  | x | x | x
| High line resistance detection |  |  |  | x | x | x
System Functions Legend
| Config: Short circuit = ALARM |  | Short circuit is interpreted as alarm (some devices on the line generate a short circuit as an alarm notification). See remark R14.
| Config: Pulse memory |  | For each line, an alarm verification can be chosen (1- or 2-stage). This function is helps to improve false-alarm immunity for automatic detectors.
| Config: "Nordic" option |  | MCP (alarm = short circuit) and automatic devices ('Cerberus collective dialect' alarm with a ~ 5,6 V Z-Diode) can be mixed. If this option is activated, a short circuit is interpreted as a manual alarm and a 'Cerberus collective dialect' alarm as an automatic alarm.
| Config: "Automatic / manual discrimination" option |  | Alarm of MCP (device type 'collective') and automatic devics (device type 'conventional') can be distingushed.
| Config: British standard |  | Generates a failure when a device is taken out of its base. All other devices on the line are still working.
Device Functions Legend
| Connection factor (KMK) |  | The connection factor depends on the device. The average current consumption is defined as KMK x 100uA.
| Connection factor (KMK) |  | The connection factor depends on the device.
Maxmimum KMK summ per zone =
| alarm = short circuit |  | Device creates a short circuit in case of an alarm.
General Legend
x | compatible
(x) | not promoted/deliverable but technically feasible
R | Restrictions apply, see comment or restriction sheet
0 | not compatible
(0) | not promoted/deliverable but technically feasible
n | not applicable
no data available
nv | not verified/compatibility not sure
Notes:
| N2 | Depends on the country regulations if allowed

## Collective restrictions
Collective Devices List of Restrictions |  | Special Test effort Prio 1 / 2 / 3;
Reference | Restriction
R3 | Connection factor 1, with higher temperature up to 3.5. See detector documentation.
R4 | On some old device lists, for some particular devices, different KMK values can be found compared to this list. Those values were valid only for old systems.
This list refers to the real current published in the detector datasheet. For calculations the new value on this list shall be used.
R5 | For this detector type, alarm verification (Config: Pulse memory) is not recommended. Reason: This detector either has an own integrated alarm evaluation or a long alarm delay time.
R6 | Both, sender (A2400S) and receiver (A2400E) have a KMK=15.
R8 | Version >30: KMK=1.25 or 1.5, depending on the parameters. See detector documentation.
R9 | There is a technical limitation for a line with resistor EOL's: To avoid line faults, the maximum number of this detector-type on one line is limited to 16.
R11 | Maximum 1 device, no other devices on the same stub are allowed.
R12 | Terminating resistors are not in compliance with the standard and result in what are known as "gray zones". These terminations are only used for modernizations.
"Gray zone" is understood to mean cases where the line driver does not reliably detect an alarming detector or other line conditions because the line resistance is too high.
R13 | Only compatible with mechanical base Z94.
R14 | System function "Short circuit = Alarm" is not allowed if there are Sinteso Multiprotocol detectors on the line. They open their isolator
on short circuit resulting that detectors behind this isolation are now longer visible and therefore no alarm would be detected!
R16 | Switchover from C-NET to collective can create resettable failure or alarm. Prevention possible with DC source (e.g. 24 V - see product documentation)
R20 | KMK=1 or 1.25, depending on the parameter set. See detector documentation.
R36 | Alarm load must be 'short circuit'
R37 | SDF200 and SDT210 not supported
R38 | The maximum number of this base-type on one line is limited to 19.